## Slide 1
ALLOTROPE
Vietnam TOU Tariff 2026
Revenue Impact Analysis — Old vs New Schedule Comparison
Emivest & Ecoplexus 40MW Cases
April 2026

## Slide 2
01
Tariff Change Summary
Confidential — For Internal Use by Allotrope & Key Partners — Not for Further Circulation

## Slide 3
Tariff Change Summary
Vietnam TOU schedule effective April 22, 2026
Attribute | Old (≤ Apr 21) | New (≥ Apr 22)
Off-Peak (Mon–Sat) | 22:00–04:00 | 00:00–06:00
Normal (Mon–Sat) | 04:00–09:30, 11:30–17:00, 20:00–22:00 | 06:00–17:30, 22:30–24:00
Peak (Mon–Sat) | 09:30–11:30 and 17:00–20:00 | 17:30–22:30
Sunday | Normal 04:00–22:00 / Off-Peak 22:00–04:00 | Normal 06:00–24:00 / Off-Peak 00:00–06:00
BESS cycles/day | 2 (morning + evening peak) | 1 (evening peak only)
Lost
Morning Peak Solar Uplift
2→1
BESS Cycles Per Day
17:30–22:30
New Single Peak Block
Confidential — For Internal Use by Allotrope & Key Partners — Not for Further Circulation

## Slide 4
02
BESS Dispatch Impact
Confidential — For Internal Use by Allotrope & Key Partners — Not for Further Circulation

## Slide 5
BESS Dispatch Impact
Old Schedule (2 Cycles/Day)
• Charge: Off-peak 22:00–04:00
• Peak 1: 09:30–11:30 (morning solar + BESS)
• Charge 2: Normal 11:30–17:00 (from solar)
• Peak 2: 17:00–20:00 (evening BESS)
New Schedule (1 Cycle/Day)
• Charge: Off-peak 00:00–06:00 (grid only)
• Peak: 17:30–22:30 (evening BESS only)
• Solar (06:00–17:30) now fully Normal hours
• BESS preserves SOC through afternoon
-50%
BESS Cycles Per Day
~5hr
Peak Solar Overlap Lost
5hr
Evening Peak Duration
Confidential — For Internal Use by Allotrope & Key Partners — Not for Further Circulation

## Slide 6
03
Emivest Case Results
Confidential — For Internal Use by Allotrope & Key Partners — Not for Further Circulation

## Slide 7
Emivest — Revenue Impact (All PPA Options)
Old baseline revenue: $562,144
PPA Option | New Revenue | Delta $ | Delta % | Δ IRR | Δ NPV
Bundled Discount | $498,839 | -$63,305 | -11.3% | -3.25pp | -$659,445
Separate PV+BESS | $525,804 | -$36,341 | -6.5% | -1.70pp | -$323,683
DPPA (CfD) | $542,467 | -$19,677 | -3.5% | -0.76pp | -$116,188
Fixed EVN PPA | $556,068 | -$6,076 | -1.1% | +0.00pp | +$53,174
-$63,305
Worst Hit (Bundled Discount)
-$6,076
Best Preserved (Fixed PPA)
Confidential — For Internal Use by Allotrope & Key Partners — Not for Further Circulation

## Slide 8
Emivest — Revenue Decomposition by Driver
Bundled Discount option — root cause breakdown
Driver | Impact | Explanation
Loss of morning peak uplift | -$65,343 | Solar kWh (09:30–11:30) now earns Normal rate
BESS cycle reduction | -$32,609 | Single cycle halves BESS arbitrage revenue
Shifted peak window (timing) | +$34,640 | Later peak extends discharge into higher-load hours
Off-peak rate changes | +$7 | Minimal effect due to low off-peak consumption
Confidential — For Internal Use by Allotrope & Key Partners — Not for Further Circulation

## Slide 9
04
Ecoplexus 40MW Results
Confidential — For Internal Use by Allotrope & Key Partners — Not for Further Circulation

## Slide 10
Ecoplexus 40MW — DPPA (CfD) Impact
Metric | Old Tariff | New Tariff | Delta
Year 1 Revenue | $5,543,642 | $6,891,647 | +$1,348,006 (+24.3%)
Project IRR | 6.26% | 9.31% | +3.06 pp
Equity IRR | 5.71% | 8.70% | +2.99 pp
NPV | $6,009,427 | $17,808,162 | +$11,798,735 (+196%)
Min DSCR | 1.28x | 1.27x | -0.01x (stable)
Year 1 DPPA Rev | $2,547,079 | $3,166,432 | +$619,353 (+24.3%)
Year 1 Grid Savings | $2,996,563 | $3,725,215 | +$728,652 (+24.3%)
9.31%
New Project IRR
+$11.8M
NPV Gain
+24.3%
Revenue Uplift
Why Ecoplexus gains: Larger solar+BESS system benefits from later peak timing (17:30–22:30) with higher evening load coincidence. DPPA CfD settlement amplifies the tariff spread.
Confidential — For Internal Use by Allotrope & Key Partners — Not for Further Circulation

## Slide 11
05
Mitigations & Next Steps
Confidential — For Internal Use by Allotrope & Key Partners — Not for Further Circulation

## Slide 12
Recommended Mitigations
R Re-price PPA offers — Adjust bundled and DPPA offers against the lower evening-only uplift.
Solar no longer touches any peak block.
D Re-tune BESS dispatch — Focus on evening peak capture. Preserve SOC during late-afternoon standard hours.
C Review discount assumptions — Separate PV-heavy vs BESS-heavy product stacks.
The tariff shift impacts them differently.
K Maintain both tariff baselines — Keep old/new regression artifacts until 2026 schedule
becomes the production default for all project types.
S Sensitivity analysis — Evaluate strike price and discount adjustments under the new schedule.
Confidential — For Internal Use by Allotrope & Key Partners — Not for Further Circulation

## Slide 13
Summary & Key Takeaways
Metric | Emivest (Worst) | Emivest (Best) | Ecoplexus
Revenue Delta | -$63,305 (-11.3%) | -$6,076 (-1.1%) | +$1,348,006 (+24.3%)
Project IRR Delta | -3.25 pp | +0.00 pp | +3.06 pp
NPV Delta | -$659,445 | +$53,174 | +$11,798,735
DSCR Impact | 1.96x → 1.64x | 1.96x → 1.93x | 1.28x → 1.27x
Key Messages:
• Small C&I (Emivest) is negatively impacted — hardest for Bundled Discount (-11.3% revenue)
• Large utility-scale (Ecoplexus) benefits significantly (+24% revenue, +3pp IRR)
• Fixed EVN PPA is the most resilient option for Emivest under the new schedule
• BESS dispatch strategy must be updated — the old 2-cycle pattern is no longer optimal
Confidential — For Internal Use by Allotrope & Key Partners — Not for Further Circulation